Equipment Maintenance

ICE-MAKER

Overview

To keep the overall operating cost down and efficiency up, regular preventative maintenance to ice-makers is essential.

| Task | Who | Frequency |
| --- | --- | --- |
| 1. Cleaning Air Filters (air-cooled units) | Owner | Monthly |
| 2. Clean Condenser | Owner | Monthly |
| 3. Clean Storage Bin | Owner | Quarterly |
| 4. Clean Evaporator and Reservoir | Owner | Quarterly |
| 5. Yearly Inspection & Cleaning | Trained Professional Service Technician | Yearly |

Task Procedures

- Cleaning the air filter give adequate airflow across the condenser, resulting in maximum operating efficiency.  Most filters can be cleaned with warm soapy water.  Consult your operations manual for your specific machine.

- Clean the condenser coil with a soft nylon brush and vacuum up the dirt or blow out with compressed air.  Never use a wire brush to clean condenser fins.

- Remove all ice from the storage bin and clean with a neutral cleaner.  Rinse thoroughly after cleaning.  Check and replace water filter if required.

- Inspect and clean water valve inlet screen.  Wipe out the reservoir with a neutral cleaner and rinse thoroughly.  Check the evaporator for calcium and lime deposits.  Check the interior of the unit for unusual oil spots and water drips.  Address any findings before a problem occurs.

- Equipment should be professionally cleaned and inspected at least once per year.  This allows an experienced service technician a chance to thoroughly clean, sanitize as well as an opportunity to look for and detect items that may have been overlooked during self performed maintenance.